## Summary
Minimizing Costs
Capital Costs
Annual Pipe costs | 76521.615 | $/year
Annual Tank costs | 0 | $/year
Annual Pump costs | 8266 | $/year
Diesel Generator costs | 42200 | $/year
Valve cost | 323 | $/year
Total Annual capital costs | 127310.615 | $/year
Operational cost
Annual Pumping cost | 211529.088 | $/year
TOTAL Annual costs | 338839.703 | $/year
Minimizing GHG emissions
Capital GHG
Annual Pipe GHG | 71816.9828 | kgCO2-e/year
Operational GHG
Annual Pumping GHG | 1988992 | kgCO2-e/year
TOTAL Annual GHG | 2060808.9828 | kgCO2-e/year
Minimizing Water Age
WAnet value | 0.30963

## PipeDesign
Pipe ID | Pipe Diameter | Pipe Length | Pipe Cost/m | Pipe Cost | GHG/m | GHG
| mm | m | $/m/year | $/year | kgCO2-e/m/year | kgCO2-e/year
Pipe PP100 | 457 | 107.88 | 26.65 | 2875.002 | 38.35 | 4137.198
Pipe PP1000 | 152 | 109.27 | 12.1 | 1322.167 | 9.71 | 1061.0117
Pipe PP1024 | 102 | 375.62 | 9.97 | 3744.9314 | 5.9 | 2216.158
Pipe PP1044 | 152 | 65.8 | 12.1 | 796.18 | 9.71 | 638.918
Pipe PP115 | 102 | 99.88 | 9.97 | 995.8036 | 5.9 | 589.292
Pipe PP144 | 152 | 130.79 | 12.1 | 1582.559 | 9.71 | 1269.9709
Pipe PP184 | 102 | 59.38 | 9.97 | 592.0186 | 5.9 | 350.342
Pipe PP22 | 457 | 567.3 | 26.65 | 15118.545 | 38.35 | 21755.955
Pipe PP245 | 203 | 18.65 | 14.49 | 270.2385 | 13.94 | 259.981
Pipe PP397 | 254 | 13.16 | 15.55 | 204.638 | 18.43 | 242.5388
Pipe PP398 | 203 | 6.75 | 14.49 | 97.8075 | 13.94 | 94.095
Pipe PP399 | 254 | 9.71 | 15.55 | 150.9905 | 18.43 | 178.9553
Pipe PP403 | 203 | 6.86 | 14.49 | 99.4014 | 13.94 | 95.6284
Pipe PP409 | 203 | 26.38 | 14.49 | 382.2462 | 13.94 | 367.7372
Pipe PP445 | 356 | 7.8 | 19.94 | 155.532 | 28.09 | 219.102
Pipe PP465 | 203 | 18.2 | 14.49 | 263.718 | 13.94 | 253.708
Pipe PP467 | 203 | 15.17 | 14.49 | 219.8133 | 13.94 | 211.4698
Pipe PP752 | 152 | 70.36 | 12.1 | 851.356 | 9.71 | 683.1956
Pipe PP787 | 152 | 127.08 | 12.1 | 1537.668 | 9.71 | 1233.9468
Pipe PP788 | 152 | 107.85 | 12.1 | 1304.985 | 9.71 | 1047.2235
Pipe PP791 | 203 | 82.5 | 14.49 | 1195.425 | 13.94 | 1150.05
Pipe PP813 | 102 | 30.85 | 9.97 | 307.5745 | 5.9 | 182.015
Pipe PP815 | 254 | 50.52 | 15.55 | 785.586 | 18.43 | 931.0836
Pipe PP853 | 203 | 295.68 | 14.49 | 4284.4032 | 13.94 | 4121.7792
Pipe PP915 | 356 | 10.58 | 19.94 | 210.9652 | 28.09 | 297.1922
Pipe PP981 | 152 | 36.19 | 12.1 | 437.899 | 9.71 | 351.4049
Pipe PP995 | 254 | 228.99 | 15.55 | 3560.7945 | 18.43 | 4220.2857
Pipe PP996 | 305 | 10.22 | 18.28 | 186.8216 | 23.16 | 236.6952
1 | 102 | 328.74 | 8.31 | 2731.8294 | 5.9 | 1939.566
2 | 102 | 328.98 | 8.31 | 2733.8238 | 5.9 | 1940.982
3 | 102 | 113.05 | 8.31 | 939.4455 | 5.9 | 666.995
4 | 102 | 310.4 | 8.31 | 2579.424 | 5.9 | 1831.36
5 | 102 | 231.1 | 8.31 | 1920.441 | 5.9 | 1363.49
6 | 102 | 218.93 | 8.31 | 1819.3083 | 5.9 | 1291.687
7 | 102 | 259.37 | 8.31 | 2155.3647 | 5.9 | 1530.283
8 | 102 | 470.52 | 8.31 | 3910.0212 | 5.9 | 2776.068
9 | 102 | 244.52 | 8.31 | 2031.9612 | 5.9 | 1442.668
10 | 102 | 393.42 | 8.31 | 3269.3202 | 5.9 | 2321.178
11 | 102 | 314.33 | 8.31 | 2612.0823 | 5.9 | 1854.547
12 | 102 | 240.65 | 8.31 | 1999.8015 | 5.9 | 1419.835
13 | 102 | 293.73 | 8.31 | 2440.8963 | 5.9 | 1733.007
14 | 102 | 221.76 | 8.31 | 1842.8256 | 5.9 | 1308.384
TOTAL |  |  |  | 76521.615 |  | 71816.9828
Note: This sheet refers to both new pipes and parallel pipes. Add additional rows into the table as required (as for all other sheets).

## TankDesign
Tank ID | Added Volume | Tank Cost
| m3 | $
0 | 0 | 0
TOTAL |  | 0

## PumpDesign
Pump ID | Pump Curve | Pump Cost
$
PPU1 | 8 | 4133
PPU2 | 8 | 4133
TOTAL |  | 8266

## ValveDesign
Valve ID | Valve Cost
$
N15 | 323
TOTAL | 323
Note: insert 0 (zero) if the valve N15 is not inserted

## DieselGenerator
Diesel Generator No | Max Power | Pump ID | Max Pump Power | Dies. Gen. Cost | Check Max Power
|  |  | kW | $/year
1 | 200 | PU2 | 45.24 | 11630 | ok
|  | PU3 | 45.24
|  | PPU1 | 45.24
|  | PPU2 | 45.24
2 | 100 | PU6 | 49.76 | 10560 | ok
|  | PU7 | 49.76
3 | 100 | PU8 | 31.67 | 10560 | ok
|  | PU9 | 31.67
4 | 50 | PU10 | 22.62 | 9450 | ok
|  | PU11 | 22.62
TOTAL |  |  |  | 42200
EXAMPLE:
In this example, only PU1, PU2, PU3 and PU8 are linked to a diesel generator and they will be operating during the 2 hours of power outage.
All other pumps will be switched off for those 2 hours.
Diesel Generator No | Max Power | Pump ID | Max Pump Power | Dies. Gen. Cost | Check Max Power
|  |  | kW | $/year
1 | 200 | PU1 | 45.24 | 11630 | ok
|  | PU2 | 45.24
|  | PU3 | 45.24
2 | 200 | PU8 | 31.67 | 11630 | ok
TOTAL |  |  |  | 23260