## Summary
Minimizing Costs
Capital Costs
Annual Pipe costs | 138994.945 | $/year
Annual Tank costs | 30640 | $/year
Annual Pump costs | 33422 | $/year
Diesel Generator costs | 50540 | $/year
Valve cost | 0 | $/year
Total Annual capital costs | 253596.945 | $/year
Operational cost
Annual Pumping cost | 166940 | $/year
TOTAL Annual costs | 420536.945 | $/year
Minimizing GHG emissions
Capital GHG
Annual Pipe GHG | 165309.8384 | kgCO2-e/year
Operational GHG
Annual Pumping GHG | 1423103 | kgCO2-e/year
TOTAL Annual GHG | 1588413 | kgCO2-e/year
Minimizing Water Age
WAnet value | 0

## PipeDesign
Pipe ID | Pipe Diameter | Pipe Length | Pipe Cost/m | Pipe Cost | GHG/m | GHG
| mm | m | $/m/year | $/year | kgCO2-e/m/year | kgCO2-e/year
1 | 102 | 328.74 | 8.31 | 2731.8294 | 5.9 | 1939.566
2 | 102 | 328.98 | 8.31 | 2733.8238 | 5.9 | 1940.982
3 | 102 | 113.05 | 8.31 | 939.4455 | 5.9 | 666.995
4 | 102 | 310.4 | 8.31 | 2579.424 | 5.9 | 1831.36
5 | 102 | 231.1 | 8.31 | 1920.441 | 5.9 | 1363.49
6 | 102 | 218.93 | 8.31 | 1819.3083 | 5.9 | 1291.687
7 | 102 | 259.37 | 8.31 | 2155.3647 | 5.9 | 1530.283
8 | 102 | 470.52 | 8.31 | 3910.0212 | 5.9 | 2776.068
9 | 102 | 244.52 | 8.31 | 2031.9612 | 5.9 | 1442.668
10 | 102 | 393.42 | 8.31 | 3269.3202 | 5.9 | 2321.178
11 | 102 | 314.33 | 8.31 | 2612.0823 | 5.9 | 1854.547
12 | 102 | 240.65 | 8.31 | 1999.8015 | 5.9 | 1419.835
13 | 102 | 293.73 | 8.31 | 2440.8963 | 5.9 | 1733.007
14 | 102 | 221.76 | 8.31 | 1842.8256 | 5.9 | 1308.384
P1024 | 102 | 375.62 | 9.97 | 3744.9314 | 5.9 | 2216.158
P302 | 254 | 178.28 | 15.55 | 2772.254 | 18.43 | 3285.7004
PP100 | 508 | 107.88 | 29.58 | 3191.0904 | 43.76 | 4720.8288
PP102 | 457 | 1280.3 | 26.65 | 34119.995 | 38.35 | 49099.505
PP159 | 203 | 118.78 | 14.49 | 1721.1222 | 13.94 | 1655.7932
PP17 | 406 | 32.42 | 23.26 | 754.0892 | 33.09 | 1072.7778
PP184 | 152 | 59.38 | 12.1 | 718.498 | 9.71 | 576.5798
PP21 | 254 | 176.48 | 15.55 | 2744.264 | 18.43 | 3252.5264
PP22 | 508 | 567.3 | 29.58 | 16780.734 | 43.76 | 24825.048
PP23 | 508 | 316.91 | 29.58 | 9374.1978 | 43.76 | 13867.9816
PP235 | 254 | 92.74 | 15.55 | 1442.107 | 18.43 | 1709.1982
PP24 | 406 | 71.05 | 23.26 | 1652.623 | 33.09 | 2351.0445
PP25 | 406 | 4.3 | 23.26 | 100.018 | 33.09 | 142.287
PP251 | 254 | 11.49 | 15.55 | 178.6695 | 18.43 | 211.7607
PP295 | 102 | 133.23 | 9.97 | 1328.3031 | 5.9 | 786.057
PP307 | 254 | 47.3 | 15.55 | 735.515 | 18.43 | 871.739
PP34 | 457 | 98 | 26.65 | 2611.7 | 38.35 | 3758.3
PP378 | 203 | 6.47 | 14.49 | 93.7503 | 13.94 | 90.1918
PP397 | 305 | 13.16 | 18.28 | 240.5648 | 23.16 | 304.7856
PP398 | 254 | 6.75 | 15.55 | 104.9625 | 18.43 | 124.4025
PP399 | 254 | 9.71 | 15.55 | 150.9905 | 18.43 | 178.9553
PP445 | 102 | 7.8 | 9.97 | 77.766 | 5.9 | 46.02
PP467 | 102 | 15.17 | 9.97 | 151.2449 | 5.9 | 89.503
PP468 | 203 | 31.29 | 14.49 | 453.3921 | 13.94 | 436.1826
PP53 | 254 | 10.32 | 15.55 | 160.476 | 18.43 | 190.1976
PP752 | 152 | 70.36 | 12.1 | 851.356 | 9.71 | 683.1956
PP788 | 203 | 107.85 | 14.49 | 1562.7465 | 13.94 | 1503.429
PP791 | 254 | 82.5 | 15.55 | 1282.875 | 18.43 | 1520.475
PP796 | 203 | 22.42 | 14.49 | 324.8658 | 13.94 | 312.5348
PP813 | 203 | 30.85 | 14.49 | 447.0165 | 13.94 | 430.049
PP815 | 254 | 50.52 | 15.55 | 785.586 | 18.43 | 931.0836
PP915 | 203 | 10.58 | 14.49 | 153.3042 | 13.94 | 147.4852
PP934 | 254 | 18.46 | 15.55 | 287.053 | 18.43 | 340.2178
PP988 | 102 | 9.74 | 9.97 | 97.1078 | 5.9 | 57.466
PP99 | 406 | 452.37 | 23.26 | 10522.1262 | 33.09 | 14968.9233
PP96 | 356 | 10.22 | 19.94 | 203.7868 | 28.09 | 287.0798
PP97 | 254 | 154.87 | 15.55 | 2408.2285 | 18.43 | 2854.2541
PP98 | 254 | 107.98 | 15.55 | 1679.089 | 18.43 | 1990.0714
TOTAL |  |  |  | 138994.945 |  | 165309.8384
Note: This sheet refers to both new pipes and parallel pipes. Add additional rows into the table as required (as for all other sheets).

## TankDesign
Tank ID | Added Volume | Tank Cost
| m3 | $
T4 | 1000 | 30640
TOTAL |  | 30640

## PumpDesign
Pump ID | Pump Curve | Pump Cost
$
PU1 | 10a | 3307
PU2 | 8b | 4554
PU3 | 10a | 3307
PU6 | 10a | 3307
PU7 | 8b | 4554
PU10 | 10a | 3307
PUN1 | 8b | 4554
PUN2 | 8a | 3225
PUN4 | 10a | 3307
TOTAL |  | 33422

## ValveDesign
Valve ID | Valve Cost
$
N15 | 0
TOTAL | 0
Note: insert 0 (zero) if the valve N15 is not inserted

## DieselGenerator
Diesel Generator No | Max Power | Pump ID | Max Pump Power | Dies. Gen. Cost | Check Max Power
|  |  | kW | $/year
1 | 200 | PU1 | 24.88 | 11630 | ok
|  | PU2 | 54.28
|  | PU3 | 24.88
|  | PUN1 | 54.28
2 | 50 | PUN2 | 22.62 | 9450 | ok
3 | 100 | PU6 | 24.88 | 10560 | ok
|  | PU7 | 54.28
4 | 50 | PUN4 | 24.88 | 9450 | ok
5 | 50 | PU10 | 24.88 | 9450 | ok
|  | PU11 | 22.62
TOTAL |  |  |  | 50540
EXAMPLE:
In this example, only PU1, PU2, PU3 and PU8 are linked to a diesel generator and they will be operating during the 2 hours of power outage.
All other pumps will be switched off for those 2 hours.
Diesel Generator No | Max Power | Pump ID | Max Pump Power | Dies. Gen. Cost | Check Max Power
|  |  | kW | $/year
1 | 200 | PU1 | 45.24 | 11630 | ok
|  | PU2 | 45.24
|  | PU3 | 45.24
2 | 200 | PU8 | 31.67 | 11630 | ok
TOTAL |  |  |  | 23260