## Summary
Minimizing Costs
Capital Costs
Annual Pipe costs | 127318 | $/year
Annual Tank costs | 58680 | $/year
Annual Pump costs | 8472 | $/year
Diesel Generator costs | 38910 | $/year
Valve cost | 0 | $/year
Total Annual capital costs | 233380 | $/year
Operational cost
Annual Pumping cost | 1319915 | $/year
TOTAL Annual costs | 1553295 | $/year
Minimizing GHG emissions
Capital GHG
Annual Pipe GHG | 146767.86 | kgCO2-e/year
Operational cost
Annual Pumping GHG | 2037164 | kgCO2-e/year
TOTAL Annual GHG Emissions | 2183931.86 | kgCO2-e/year
Minimizing Water Age
WAnet value | 0.11

## PipeDesign
Pipe ID | Pipe Diameter | Pipe Length | Pipe Cost/m | Pipe Cost | GHG/m | GHG
| mm | m | $/m/year | $/year | kgCO2-e/m/year | kgCO2-e/year
1 | 102 | 328.74 | 8.31 | 2731.83 | 5.9 | 1939.57
2 | 0 | 328.98 | 0 | 0 | 0 | 0
3 | 102 | 113.05 | 8.31 | 939.45 | 5.9 | 667
4 | 102 | 310.4 | 8.31 | 2579.42 | 5.9 | 1831.36
5 | 102 | 231.1 | 8.31 | 1920.44 | 5.9 | 1363.49
6 | 102 | 218.93 | 8.31 | 1819.31 | 5.9 | 1291.69
7 | 102 | 259.37 | 8.31 | 2155.36 | 5.9 | 1530.28
8 | 102 | 470.52 | 8.31 | 3910.02 | 5.9 | 2776.07
9 | 102 | 244.52 | 8.31 | 2031.96 | 5.9 | 1442.67
10 | 102 | 393.42 | 8.31 | 3269.32 | 5.9 | 2321.18
11 | 102 | 314.33 | 8.31 | 2612.08 | 5.9 | 1854.55
12 | 102 | 240.65 | 8.31 | 1999.8 | 5.9 | 1419.84
13 | 102 | 293.73 | 8.31 | 2440.9 | 5.9 | 1733.01
14 | 102 | 221.76 | 8.31 | 1842.83 | 5.9 | 1308.38
PP22 | 711 | 567.3 | 48.12 | 27298.47 | 66.57 | 37765.16
PP23 | 711 | 316.91 | 48.12 | 15249.71 | 66.57 | 21096.7
PP100 | 508 | 107.88 | 29.58 | 3191.09 | 43.76 | 4720.83
PP20 | 457 | 579.67 | 26.65 | 15448.21 | 38.35 | 22230.34
PP853 | 356 | 295.68 | 19.94 | 5895.86 | 28.09 | 8305.65
PP995 | 305 | 228.99 | 18.28 | 4185.94 | 23.16 | 5303.41
PP1045 | 305 | 68.63 | 18.28 | 1254.56 | 23.16 | 1589.47
PP15 | 305 | 395.29 | 18.28 | 7225.9 | 23.16 | 9154.92
PP752 | 254 | 70.36 | 15.55 | 1094.1 | 18.43 | 1296.73
PP347 | 254 | 385.56 | 15.55 | 5995.46 | 18.43 | 7105.87
PP96 | 203 | 53.72 | 14.49 | 778.4 | 13.94 | 748.86
PP527 | 152 | 149.04 | 12.1 | 1803.38 | 9.71 | 1447.18
PP787 | 102 | 127.08 | 9.97 | 1266.99 | 5.9 | 749.77
PP295 | 102 | 133.23 | 9.97 | 1328.3 | 5.9 | 786.06
PP144 | 102 | 130.79 | 9.97 | 1303.98 | 5.9 | 771.66
PP1024 | 102 | 375.62 | 9.97 | 3744.93 | 5.9 | 2216.16
TOTAL |  |  |  | 127318 |  | 146767.86
Note: This sheet refers to both new pipes and parallel pipes.
Parallel pipes are labelled with "P" in front of existing pipe ID, for instance PP96 is the parellel pipe for exsiting pipe P96

## TankDesign
Tank ID | Added Volume | Tank Cost
| m3 | $
T4 | 1000 | 30640
T5 | 500 | 14020
T7 | 500 | 14020
TOTAL |  | 58680

## PumpDesign
Pump ID | Pump Curve | Pump Cost
$
PU1a | 8 | 4133
PU6a | 10 | 4339
TOTAL |  | 8472

## ValveDesign
Valve ID | Valve Cost
$
N15 | 0
TOTAL
Note: insert 0 (zero) if the valve N15 is not inserted

## DieselGenerator
Diesel Generator No | Max Power | Pump ID | Max Pump Power | Dies. Gen. Cost | Check Max Power
|  |  | kW | $/year
1 | 100 | PU1 | 45.24 | 10560 | ok
|  | PU2 | 45.24
2 | 50 | PU6 | 49.76 | 9450 | ok
3 | 50 | Pu8 | 31.67 | 9450 | ok
4 | 50 | Pu10 | 22.62 | 9450 | ok
|  | PU11 | 22.62
TOTAL |  |  |  | 38910